भारतीय लघु उद्योग विकास बैंक

Small Industries Development Bank of India

Request for Proposal for Co-location of Bank’s

Disaster Recovery Site - Annexures

सिडबी की डिजास्टर रिकवरी (डीआर) साईट -

को-लोकेशन हेतु प्रस्ताव के लिए अनुरोध - संलग्नक

| टेंडर सं. / Tender No. | 400/2019/1338/BYO/ITV |
| --- | --- |
| टेंडर जारी करने की तिथि / Tender Issue Date | May 29, 2018 |
| बोली जमा करनी की अंतिम तिथि / Last date for bid submission | June 18, 2018 |
| बयाना जमा राशि / Earnest Money Deposit (Refundable without Interest) | `3.50 Lakh (Rupees Three Lakh Fifty Thousand only) |
| टेंडर मूल्य /Tender Cost(Non Refundable) | ` 5,000/- (Rupees Five Thousand only) |

भारतीय लघु उद्योग विकास बैंक

एमएसएमई विकास केन्द्र, सी-11, जी ब्लाक,

बांद्रा कुर्ला काम्प्लेक्स, बांद्रा (पू.), मुम्बई – 400051

SMALL INDUSTRIES DEVELOPMENT BANK OF INDIA

MSME Development Center, C-11, ‘G’ Block,

Bandra Kurla Complex, Bandra (E), Mumbai - 400 051

Table of Contents

1.	Annexures	3

1.1.	Annexure – I: Bid Forwarding Letter	4

1.2.	Annexure –II: Minimum Eligibility Criteria	5

1.3.	Annexure –III: Technical Bid	10

1.4.	Annexure –IV: Commercial Bid	18

1.5.	Annexure –V: Power of Attorney	22

1.6.	Annexure –VI: Non-Blacklisting	23

1.7.	Annexure –VII: EMD / Bid Security Form	24

1.8.	Annexure –VIII: Pre-Contract Integrity Pact	26

1.9.	Annexure -IX: Undertaking from Bidder Regarding Ownership of Site	32

1.10.	Annexure –X: Statement of Deviations	34

1.11.	Annexure –XI: Bank Mandate Form	35

1.12.	Annexure -XII: Compliance Statement	36

1.13.	Annexure –XIII: Non-Disclosure Agreement	37

1.14.	Annexure –XIV: Performance Guarantee Format	38

1.15.	Annexure –XV: Contract Form	40

2.	APPENDIX	42

2.1.	Appendix -i:- Requirement of Inter-rack Cabling	43

2.2.	Appendix -ii: - List of Hardware Items with Power Socket Details	44

# Annexures

  - Annexure – I: Bid Forwarding Letter

(To be submitted on Bidder’s letter head)

Date:

The Dy. General Manager (Systems)

Small Industries Development Bank of India,

3rd Floor, MSME Development Centre,

Plot No. C-11, G Block

Bandra Kurla Complex (BKC), Bandra (E)

Mumbai - 400 051

Dear Sir,

Co-location and hosting Data Centre Facilities for Bank’s -

Disaster Recovery Site

We, the undersigned, offer to submit our bid in response and accordance with your tender No. 400/2019/1338/BYO/ITV dated May 29, 2018. Having examined the tender document including all Annexures carefully, we are hereby submitting our proposal along with all the requisite EMD and other documents as desired by the Bank.

If our Bid for the above job is accepted, we undertake to enter into and execute at our cost, when called upon by the Bank to do so, a contract in the prescribed form. Unless and until a formal contract is prepared and executed, this bid together with your written acceptance thereof shall constitute a binding contract between us.

Further, we agree to abide by all the terms and conditions as mentioned herein the tender document.

We agree to abide by this offer till 180 days from the date of last day for submission of offer (Bid).

We agree that, the rates quoted by us would serve as a rate contract for future additional services.

We agree that, the Bank will pay power charges based on actual power units consumed.

We have also noted that SIDBI reserves the right to consider/ reject any or all bids without assigning any reason thereof.

We understand that the Bank is not bound to accept any proposal it receives.

Dated at ______ day of _______ 2018.

Yours sincerely,

| Date | Signature of Authorised Signatory … |
| --- | --- |
| Place | Name of the Authorised Signatory … |
|  | Designation … |
|  | Name of the Organisation … |
|  | Seal … |

  - Annexure –II: Minimum Eligibility Criteria

    - Details of Bidder

| S.N. | Particulars | Documents to be Submitted | Bidders Response (to be filled in by bidder) |
| --- | --- | --- | --- |
| 1 | Name of the bidder entity |  |  |
| 2 | Year of establishment |  |  |
| 3 | Ownership of the bidder or entity |  |  |
| 4 | Registration number and date of registration. | Copy of Registration Certificate. |  |
| 5 | Registered Office Address. |  |  |
| 6 | GST Number | Copy of GST Registration certificate |  |
| 7 | PAN No. | Copy of PAN number. |  |
| 8 | Promotor / Director Details |  |  |
| a | Name |  |  |
| b | Designation (Promoter / Director) |  |  |
| c | Mobile No. |  |  |
| d | Mail Id |  |  |
| 9 | Address of bidder Office at Chennai with contact numbers |  |  |
| a | Address |  |  |
| b | Land Line No. |  |  |
| c | Mail Id. |  |  |
| 10 | Contact Details of Bidders authorized Representative (on whose behalf Power of Attorney issued). |  |  |
| a | Name |  |  |
| b | Designation |  |  |
| c | Mobile No. |  |  |
| d | Mail id |  |  |
| e | Specimen Full Signature and initials. |  |  |
| 11 | MSME Details |  |  |
| a | Whether Bidder MSME (Yes/No) |  |  |
| b | MSME Registration No |  |  |
| c | Date till which MSME Certificate is valid. |  |  |
| d | Attested Copy of MSME Certificate attached. (Yes /No) |  |  |
| 12 | Bank Account Details |  |  |
| a | Bank Name |  |  |
| b | Account Number |  |  |
| c | IFSC Code |  |  |
| d | Account Type |  |  |
| e | Copy of Cancelled Cheque attached. (Yes /no) |  |  |
| f | Bank Mandate form as per Annexure–XI attached. (Yes/No). |  |  |

    - Financials

- Amount in Lakhs

| S.N. | Parameter → / FY↓ | Annual Turnover | Cash Profit | Networth |
| --- | --- | --- | --- | --- |
| 1 | 2014-15 |  |  |  |
| 2 | 2015-16 |  |  |  |
| 3 | 2016-17 |  |  |  |
| 4 | Audited annual reports for FY2014-15, FY 2015-16 and FY2016-17 submitted (if available). (Yes / No). |  |  |  |
| 5 | CA certificate for FY2014-15, FY 2015-16 and FY2016-17 submitted. (Yes / No). |  |  |  |

    - Eligibility Criteria

| S.N. | Criteria | Bidder Response | Proof to be Submitted |
| --- | --- | --- | --- |
| 1 | Should be either a Government Organization/ PSU/ PSE/ partnership firm or a limited Company under Indian Laws or /and an autonomous Institution approved by GOI/RBI promoted. |  | - Partnership firm: Certified copy of Partnership Deed. - Limited Company: Certified copy of Certificate of Incorporation and Certificate of Commencement of Business. - Reference of Act/Notification - For other eligible entities: Applicable documents. |
| 2 | The bidder should have minimum experience of providing DataCenter co-location services in India for last five years as on the date of the RfP. |  | Statutory auditor certificate indicating that bidder is in DataCenter co-location services in India for last five years. |
| 3 | The bidder should have a minimum average annual turnover of at least Rs.20 crore during the last three (3) financial years i.e. FY 2015, 2016 and 2017. |  | Supporting the fact, the bidder should furnish: - Audited annual reports for FY2014-15, FY 2015-16 and FY2016-17 (if available) and - Statutory Auditor certificate for FY2014-15, FY 2015-16 and FY2016-17. The Statutory Auditor certificate should clearly indicate the Turnover, Networth and Cash Profit for the FY 2015, 2016 and 2017. |
| 4 | The bidder should have positive networth and cash profit [i.e., no cash loss] in 2 years out of last 3 Financial Years i.e. FY 2015, 2016 and 2017. |  |  |
| 5 | The proposed Data Centre Premise for hosting Bank’s DR should be at Chennai and should be at least Tier-III compliant. |  | - Supporting document - publicly available information of the proposed data center along with an undertaking on a VENDOR letterhead, clearly mentioning that the Data Centre Premise is complying with tier III [or higher] requirements. - A valid certification copy from the authorised agency to be submitted. - Undertaking / declaration on bidder letter head with the details of the proposed address duly attested, signed and stamped to be submitted. |
| 6 | ISO 27001 or BS 7799-3 (Mandatory) for the bidders DataCenter offered / proposed to Bank. The certification should be in-force. |  | ISO Certification from Governing Body for each proposed DataCenter. |
| 7 | - The bidder must be providing Data center co-location and hosting facility to at least 05 Companies at its data centers in India as on RfP date. - Of the above submitted credentials, one (1) credential should be from BFSI, Organization in India who have co-located / hosted their Data Centre or Near Site or Disaster Recovery site. |  | PO or Credential letter from Companies who have hosted their DC, DR, NDR at bidders co-hosting facility mentioning that, they have taken DataCenter co-hosting facility from the VENDOR to be submitted. |
| 8 | The proposed Data center building should be owned by bidder or on lease with unexpired lease duration of at least 12 years as on RfP date. No Partnership / Consortium is allowed. |  | Self-declaration / undertaking to this effect on company's letter head signed by company’s authorized signatory |
| 9 | The bidder should not have been black-listed by any Public Financial Institutions, Public Sector Bank, RBI or IBA or any other Government agencies during the last 3 years. Bidder must certify to that effect. |  | Self-declaration / undertaking to this effect on company's letter head signed by company’s authorized signatory as per Annexure-VI. |
| 10 | A Board Resolution/ authorization letter from the board of directors or Power of Attorney authorizing the Bid signing in favour of Bidder representative who would be signing all the pages of the bid. |  | Board Resolution / authorization letter from the board of directors / or Power of Attorney as per format given in Annexure–V to be submitted. |
| 11 | The bidder should submit Pre-Contract Integrity Pact as per format provided in Annexure –VIII of the RfP. |  | Pre-Contract Integrity Pact duly signed by authorized signatory on non-judicial stamp paper of requisite value (to be borne by the bidder) as per format given in Annexure–VIII need to be enclosed. |

I certify that the above-mentioned information and the relevant annexure and enclosures are true and correct.

| Date |  |  | Signature of Authorized Signatory … |  |
| --- | --- | --- | --- | --- |
| Place |  |  | Name of the Authorized Signatory … |  |
|  |  |  | Designation … |  |
|  |  |  | Name of the Organization … |  |
|  |  |  | Seal … |  |
|  | Note | - Bidder response should be complete with all relevant documents attached. - Documentary proof, sealed and signed by authorized signatory, must be submitted - Details of clients and relevant contact details are mandatory. Bidders may take necessary approval of the clients in advance before submission of related information. SIDBI will not make any separate request for submission of such information. - SIDBI will contact the bidder referenced customer for verifications of facts, the bidder to ensure that the customer is intimated. Further in case SIDBI feels to visit the site, the bidder to take necessary approvals for the same. SIDBI will not make any separate request to the bidder’s customers. - Proposal of the bidders are liable to be rejected in case of incomplete information or non-submission of documentary proof. |  |  |

  - Annexure –III: Technical Bid

    - Technical Specifications

| S.N. | Parameters |  | Weig-htage | Bidders Response | Bidders Comments / Details of Proof attached. |
| --- | --- | --- | --- | --- | --- |
| 1 | The facility should be either owned by bidder or on lease with unexpired lease duration of 12 years as on date of RfP. |  | 5 |  |  |
| a. | Owned / Leased but exclusive Data Centre building | 5 |  |  |  |
| b. | Owned / Leased but shared with multiple tenants | 2 |  |  |  |
| c. | The bidder to submit Annexure-IX along with documents. |  |  |  |  |
| 2 | Age of Building |  | 5 |  |  |
| a. | Less than 10 years | 5 |  |  |  |
| b. | More than 10 years | 3 |  |  |  |
| 3 | The Data Centre facility building should be away from hazardous chemical materials, LPG storage areas, chemical go-downs and other storage facilities meant for dangerous commodities. |  | 3 |  |  |
| 4 | The proposed datacenter building should not be in low lying and flood prone area. |  | 3 |  |  |
| 5 | The structural strength of the proposed building should have been certified and latest report to be available. |  | 2 |  |  |
|  | Copy of report/ certificate to be attached. |  |  |  |  |
| 6 | The proposed building should be covered under comprehensive insurance on ongoing basis including risk related to earthquake, floods, fire, lightening, terrorist attacks etc. |  | 3 |  |  |
|  | Copy of last year and current year insurance report to be attached. (Yes/No) |  |  |  |  |
| 7 | The bidder proposed site should have following compliance / certifications: |  | 18 |  |  |
| a. | NFPA 70 & 75 | 3 |  |  |  |
| b. | IS 1893:1984 seismic Compliance | 3 |  |  |  |
| c. | TIA 942 compliance | 3 |  |  |  |
| d. | ISO 20000 | 3 |  |  |  |
| e. | ISO 9001 | 3 |  |  |  |
| f. | Compliance to ASHRAE Standards | 3 |  |  |  |
|  | Copy of the relevant certification for the data center service only. |  |  |  |  |
| 8 | The bidder to provide clear space area proposed / considered for Bank for: - Bank’s DR: 05 racks, scalable to 07 racks. |  | 10 |  |  |
|  | Layout Diagram of proposed site to be provided. |  |  |  |  |
| 9 | Freight Lift/ Scissor lift - The data center should have high capacity freight/ scissor lift for ease of movement of servers and high-density network devices. |  | 3 |  |  |
| 10 | The doors for the server room, communications room, and other critical areas should be fire rated for minimum 2 hours. |  | 3 |  |  |
| 11 | The server room area should have a raised floor height of minimum 2ft. |  | 3 |  |  |
| 12 | The server hall height from raised floor to false ceiling should be at least 10ft. |  | 3 |  |  |
| 13 | The false flooring in server hall should be fire resistant and tiles should be made up of Calcium Silicate. |  | 3 |  |  |
| 14 | The Data Centre Site should have microprocessor-based system to detect water leakage. |  | 3 |  |  |
| 15 | The Data Centre site should have electronic rodent control systems with operatability on varied frequency range. |  | 3 |  |  |
| 16 | All the Building Management system (BMS) activities are to be controlled centrally in a room specifically to be used for BMS activities. The vendor should manage the BMS activities on a 24*7 basis. |  | 5 |  |  |
| 17 | There should be sufficient power backups in place for running the Building Monitoring system in the event of power outage. |  | 3 |  |  |
| 18 | Each component of data centre must allow concurrent maintenance without disruption to supply of services to data halls or support areas. |  | 2 |  |  |
| 19 | The proposed data Centre space should have load bearing capacity of 1000Kg / Sq. m. |  | 5 |  |  |
| 20 | Two independent power suppliers/ substations/ Grid Level redundancy each capable of supporting the site independently. |  | 5 |  |  |
|  | Details of power arrangement to be submitted. |  |  |  |  |
| 21 | The incoming supplies from alternate power sub-stations arranged as N+1, each entering the site from diverse paths and each terminated in separate fire-resistant enclosures. |  | 10 |  |  |
|  | Whether the utility power enter the site via overhead or underground conduits and/or duct Bank’s? |  |  |  |  |
|  | Details to be submitted. |  |  |  |  |
| 22 | Diesel Tanks (for generators) - The data centre should have high capacity diesel tanks for ensuring 48-hour power backup with contracts for fuel supply on demand. |  | 3 |  |  |
| 23 | The Diesel tanks should be underground. |  | 2 |  |  |
| 24 | Generators should be capable of providing power for 48 hours and continuously even during refilling. |  | 5 |  |  |
| 25 | The entire solution should be automatic with power supply from the transformer as the primary source and automatic switchover to DG set as a secondary source without any disruption. |  | 3 |  |  |
| 26 | The design for cooling infrastructure at the data centre should be in lines with standard guidelines to support high density cooling needs. |  | 2 |  |  |
| 27 | Redundant CRAC units to facilitate High density cooling needs. |  | 5 |  |  |
| 28 | The bidder should be able to provide Auto Transfer Switch (ATS) for single power input systems. |  | 2 |  |  |
| 29 | Biometric Access to the common entry to the Server room/ Server Hall area should be available |  | 2 |  |  |
| 30 | The offered space to Bank for co-location should preferably not be top floor /ground Floor. |  | 5 |  |  |
| 31 | A separate Cage dedicated for the Bank within the server room / Server Hall area. The cage area should be rectangle or square and have sufficient space for opening of front and rear doors for installation / replacement / trouble shooting of hardware and movement of service personnel. |  | 10 |  |  |
|  | Following Details of cage area to be submitted: |  |  |  |  |
|  | a) Layout of area allocated to Bank. |  |  |  |  |
|  | b) Size of cage area proposed. |  |  |  |  |
| 32 | The server cage area entrance and exit should be accessible using the proximity card (access control) with biometric access. |  | 2 |  |  |
| 33 | The racks in cage area should be of 42U size with horizontal and vertical cable managers and the bidder to provide inter-rack cabling using patch panels, cross connects to communication area, cable managers for structured cabling, redundant power strips, earthing for each rack etc. |  | 5 |  |  |
| 34 | The bidder should be able to provide space in the same server hall for additional racks (beyond 07 racks) at the contracted rate during the period of contract. |  | 5 |  |  |
| 35 | UPS should be configured in redundant mode i.e. N+1. |  | 5 |  |  |
|  | Details of UPS arrangement to be submitted. |  |  |  |  |
| 36 | Two separate power paths from the UPS to be provided to the server / network communication room. |  | 3 |  |  |
| 37 | The bidder shall provide separate meter for measuring the electricity units consumed by the Bank for the servers/ equipment. |  | 3 |  |  |
| 38 | The proposed caged area should be well covered in the fire detection and suppression system |  | 5 |  |  |
| 39 | There should be CCTV monitoring for surveillance of the server hall area. The CCTV surveillance should cover Bank's Server / Cage area and other critical areas where Bank's components are placed. |  | 5 |  |  |
| 40 | The VENDOR shall provide dedicated IP CCTV camera(s) along with other accessories in the cage area to capture all the activities carried out at the front and back of the rack. The video feed should be made available to the Bank on-site. Further, the video feed should be stored for a period of three months. In case of any observation by the Bank’s engaged auditor (IS, ISO, Regulators etc) during the period of contract on the positioning of CCTV cameras, VENDOR has to provide additional CCTV cameras, at contracted rate. |  | 5 |  |  |
| 41 | Smoke detection and fire suppression system should cover proposed Bank's server caged area. |  | 5 |  |  |
| 42 | The temperature in the server hall should be maintained at 22 +/- 2deg C |  | 2 |  |  |
| 43 | The humidity at the data centre should be maintained at 50 % +/- 10% RH. |  | 2 |  |  |
| 44 | The server halls should have advanced fire detection & suppression system through systems like VESDA, FM 200/FE 227, NOVEC 1230 respectively |  | 2 |  |  |
| 45 | The Server room / Server Hall area should have precision air conditioning or equivalent with redundancy. |  | 2 |  |  |
| 46 | The CCTV Feeds should be provided to Bank for monitoring the cages/ its infrastructure. |  | 5 |  |  |
| 47 | Availability of 3 phase, 4 wire power system in sever hall / cage area. |  | 3 |  |  |
| 48 | The Server room area should be provided with Water Leak detection system and fire alarm system |  | 3 |  |  |
| 49 | Air Quality in the data center site should be of severity level G1 (mild) as per ISA -71.04. |  | 5 |  |  |
| 50 | Activities to be recorded and the archival should be kept |  | 5 |  |  |
| a. | Server hall CCTV (common) recording kept for more than one month. | 5 |  |  |  |
| b. | Server hall CCTV (common) recording kept for one month only. | 2 |  |  |  |
| 51 | The vendor should be able to share the video monitoring data in case required by Bank. |  | 5 |  |  |
| 52 | Entry & Exit should be restricted and monitored and should also be in CCTV surveillance coverage. |  | 2 |  |  |
| 53 | Telecom junction box, multiplexers of various service providers at least Bharti, Tata, Sify, BSNL/MTNL, Reliance to be available in and around the building. Details of service providers who’s MUXs are available at site(s) to be submitted. |  | 5 |  |  |
|  | The bidder to provide details of service provider MUX available currently in the Data Center. |  |  |  |  |
| 54 | If the Telecom junction box, multiplexers of service provider from whom Bank would be getting the links is not available then the DC service provider should allow the commissioning of the same and provide power and space without any cost to Bank. The communication room should have sufficient space for installation of additional MUX with other facilities like power. |  | 5 |  |  |
| 55 | The co-location facility VENDOR should extend the link terminated by the link service provider on the junction box till the server room where the Bank's equipment will be located. |  | 2 |  |  |
| 56 | Data centre vendor should ensure fibres from multiple providers are fed to the site from three independent channels in ring connectivity |  | 5 |  |  |
| 57 | The future link extension from the bidder communication room till the cage/rack area will be done by the bidder as per contracted rate. |  | 2 |  |  |
| 58 | 99.982% Uptime on monthly basis is required for the VENDOR Data centre. |  | 10 |  |  |
| 59 | Log reports of people accessing the Server room should be available as and when required by Bank. |  | 3 |  |  |
| 60 | Vendor shall provide the electrical cabling required by the racks to be hosted in the Data Centre |  | 2 |  |  |
| 61 | The seating area should include the desk, chair, drawer which can accommodate three box files with locking facility per seat, UPS power connections (three per seat), network connections from Bank’s server area / LAN (two per seat) etc. Vendor shall factor sufficient work area per seat. In addition, vendor shall provide adequate space for the movement within the enclosed seating area. |  | 10 |  |  |
|  | Details of seating area proposed to Bank should be submitted. |  |  |  |  |
| 62 | The Vendor shall provide Backup Tape Storage Vault Services for storing up to 100 LTO Tapes upfront and additional services for storing tapes in multiples of 25 tapes at rate contract. |  | 3 |  |  |
| 63 | The network link required between seating area and Bank's server area shall be provided by the vendor |  | 2 |  |  |
| 64 | In addition to the purchased seating area, immediate arrangement (for seating, power and network) should be made to Bank’s team of around 02 people in disaster situation to access systems hosted in DC. |  | 3 |  |  |
| 65 | Gate passes to enter Data Centre for Bank's representatives should be free of cost |  | 2 |  |  |
| 66 | The bidder should provide staging / storage area for at least four to six weeks. |  | 3 |  |  |
| 67 | Staging area should be preferably be close to the hired / hosted space and have all facilities like, redundant power, LAN connectivity, telecom | 5 | 5 |  |  |
| a. | Staging area in same floor | 5 |  |  |  |
| b. | Staging area in different floor | 2 |  |  |  |
| 68 | The bidder should provide off-site drop off and pickup facility for backup tapes. |  | 5 |  |  |
| 69 | Critical Services like power, UPS, Genset etc. are managed by: |  | 10 |  |  |
| a. | Own dedicated staff of the bidder | 10 |  |  |  |
| b. | These maintenance services are Outsourced to third party | 5 |  |  |  |
| 70 | The proposed datacenter should have multi layers of physical security: |  | 5 |  |  |
| a. | Site Perimeter (Public Zone) | 1 |  |  |  |
| b. | Perimeter Security (Reception Zone) | 1 |  |  |  |
| c. | Facility control (Operating Zone) | 1 |  |  |  |
| d. | Server Hall (high security Zone) | 2 |  |  |  |
| e. | Details of security arrangements in the Data Center to be submitted. |  |  |  |  |
|  | Total |  | 300 |  |  |

    - Reference Customer Details

- The details of existing customers to whom bidder has provided Data Center co-location/hosting facility at the site(s) proposed to the Bank’s DR.

| S.N. | Organization |  | Contact Details |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Name | Designation | Landline No. | Mobile No | Mail id |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |

- The Bank’s team would be contacting the bidder’s customers for their feedback. Hence, the bidder to take all necessary approvals from the client.

I certify that the above mentioned information and the relevant annexure and enclosures are true and correct

| Date | Signature of Authorized Signatory … |
| --- | --- |
| Place | Name of the Authorized Signatory … |
|  | Designation … |
|  | Phone & E-mail: |
|  | Name of the Organization … |
|  | Seal … |

| NOTE | - The bidder’s response column should contain the details, Yes/No will not be accepted. - The proof, wherever applicable to be attached and tag number of same to be specified in the response. - Bank shall also carry out Site visit(s) of the proposed floor in the proposed facility to verify the details and based on which marks will be awarded. - The bidder to take necessary approvals from the customers whose reference is provided to the Bank. |
| --- | --- |

  - Annexure –IV: Commercial Bid

Bank DR Site Co-location

- RECURRING CHARGES during first 05 years of contract.

- Table -1: DR Co-location [Rack Hosting, Seating Space, Dedicated IP CCTV Camera, Tape Movement and Vault services]

[Amt. in `]

| S. No. | Description | Qty. | Unit Cost Details Per Annum |  |  | Total Cost per Annum | Total Cost for Five Years |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Cost | GST | Total |  |  |
|  |  | A | B | C | D=B+C | E=DXA | F=EX5 |
| 1 | Co-location charges for DR (Racks with power strips and electrical cabling) to be hosted within the cage. | 05 |  |  |  |  |  |
| 2 | Charges for Seating Space at DR (seats). | 01 |  |  |  |  |  |
| 3 | IP CCTV camera(s) with accessories for storing the feed for a period of 03 month, providing on-site access to Bank and monitoring by the VENDOR. | 02 |  |  |  |  |  |
| 4 | Daily tape movement | 02 |  |  |  |  |  |
| 5 | Monthly Tape Movement charges. | 03 |  |  |  |  |  |
| 6 | Backup Tape Storage Vault Services for storing up to 100 LTO Tapes. | 01 |  |  |  |  |  |
| 7 | Total DR Co-location Charges for first 05 years [1+2+3+4+5+6] |  |  |  |  |  |  |

Important Note: Rate mentioned herein shall also serve as the rate contract for any additional requirement during the first five years of contract.

- Table -2: Power Charges

[Amt. in `]

| Description | kWh Per month | *Current Electricity Rate (indicative) | **Multiplication factor against the PUE for Power Charge | Annual Recurring Charge | Total Cost for Five Years |
| --- | --- | --- | --- | --- | --- |
|  | A | B | C | D=AXBXCX12 | E=DX5 |
| Power Charges - Units mentioned are in KWh per month. - Will be paid on actual usage. | 21900 | 10 |  |  |  |

* Current Electricity Rate and number of units mentioned above in the commercial bid is indicative for the TCO calculation purpose only. However, the power charges will be paid at actual subject to submission of tariff table from respective electricity service provider.

** Bidder should quote only the Multiplication Factor against the PUE for power charges to cover the electricity consumption for devices, cooling, lighting, UPS power, consumption of diesel and all associated power heads. This Multiplication factor will be fixed for the entire term of contract and extension(s), if any.

- ONE TIME CHARGES

[Amt. in `]

| S. N. | Description | Qty. | Unit Cost Details |  |  | Total Cost |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Cost | GST | Total |  |
|  |  | A | B | C | D=B+C | E = DXA |
| 1 | Caging charges to accommodate 07 racks (Lumsum). | LS |  |  |  |  |
| 2 | Inter-rack network cabling charges (per rack) | 05 |  |  |  |  |
| 3 | Cross connect charges (Copper) | 15 |  |  |  |  |
| 4 | Lift and Shift Charges (LumpSum) | LS |  |  |  |  |
| 5 | Dedicated Biometric Access Control for cage. | 01 |  |  |  |  |
| 6 | Total One Time Charges |  |  |  |  |  |

- OPTIONAL CHARGES

- During the entire period of Contract, including extended period, if any

(as and when required during the period of entire contract)

- These charges will be one-time charges, valid for the entire contract period including extended period, if any. Bank will not pay any recurring charges against these items. Quantity is for TCO calculation only.

- Order will be placed on actual requirement as and when it arise.

[Amt. in `]

| S. N. | Description | Qty. | Unit Cost Details |  |  | Total Cost |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Cost | GST | Total |  |
|  |  | A | B | C | D=B+C | E= DXA |
| 1 | Inter-rack cabling charges (per rack) | 01 |  |  |  |  |
| 2 | Cross connect charges (Copper) | 01 |  |  |  |  |
| 3 | Cross Connect Charges (Fiber) | 01 |  |  |  |  |
| 4 | Hands and Eye Support (24X7). | 01 |  |  |  |  |
| 5 | Electrical Cabling charges with socket of 32amps (single phase) | 01 |  |  |  |  |
| 6 | Electrical Cabling charges with socket of 32amps (Three phase) | 01 |  |  |  |  |
| 7 | Electrical Cabling charges with socket of 63amps (single phase) | 01 |  |  |  |  |
| 8 | Power strip with 16 numbers of IEC C-13, 10A sockets and 4 numbers of C-19, 16A sockets. (per strip) | 01 |  |  |  |  |
| 9 | Patch Panel (24 Port) – supporting 10G | 01 |  |  |  |  |
| 10 | UTP cable (supporting 10G) 1 box with laying charges | 01 |  |  |  |  |
| 11 | UTP Patch Chord (CAT6) – 5Mts | 25 |  |  |  |  |
| 12 | ATS with cabling upto rack. | 01 |  |  |  |  |
| 13 | Per annum Cost of co-location of single rack (non-caged) inclusive of network cabling from the rack to caged area and power cabling. {Power charges will be paid on actuals}. | 01 |  |  |  |  |
| 14 | Additional vaulting services for a block of 25 LTO tapes. | 01 |  |  |  |  |
| 15 | Total Optional Charges [1 to 15] |  |  |  |  |  |

- Beyond Five Years of Contract (Valid for next five years)

- DR Co-location [Rack Hosting, Seating Space, Dedicated IP CCTV Camera, Tape Movement and Vault services]

[Amt. in `]

| S. N. | Description | Qty. | Unit Cost Details per Annum |  |  | Cost per Annum | Total Cost |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Cost | GST | Total |  |  |
|  |  | A | B | C | D=B+C | E=A X D | F = E X 5 |
| 1 | Co-location charges for DR (Racks with power strips and electrical cabling) to be hosted within the cage. | 05 |  |  |  |  |  |
| 2 | Charges for Seating Space at DR (seats). | 01 |  |  |  |  |  |
| 3 | IP CCTV camera(s) with accessories for storing the feed for a period of 3 month, providing online access to Bank and monitoring by the VENDOR. | 02 |  |  |  |  |  |
| 4 | Daily tape movement | 02 |  |  |  |  |  |
| 5 | Monthly Tape Movement charges. | 03 |  |  |  |  |  |
| 6 | Backup Tape Storage Vault Services for storing up to 100 LTO Tapes | 01 |  |  |  |  |  |
| 7 | Total DR Co-location Charges for next 05 years [1+2+3+4+5+6] |  |  |  |  |  |  |

Important Note: Rate mentioned herein shall also serve as the rate contract for any additional requirement during the first five years of contract.

- Power Charges

[Amt. in `]

| Description | kWh per Month | *Current Electricity Rate (indicative) | **Multiplication factor against the PUE for Power Charge | Annual Recurring Charge | Total Cost for Five Years |
| --- | --- | --- | --- | --- | --- |
|  | A | B | C | D=AXBXCX12 | E=DX5 |
| Power Charges - Units mentioned are in KWh per month. - Will be paid on actual usage. | 21900 | 10 |  |  |  |

* Current Electricity Rate and number of units mentioned above in the commercial bid is indicative for the TCO calculation purpose only. However, the power charges will be paid at actual subject to submission of tariff table from respective electricity service provider.

** Bidder should quote only the Multiplication Factor against the PUE for power charges to cover the electricity consumption for devices, cooling, lighting, UPS power, consumption of diesel and all associated power heads. This Multiplication factor will be fixed for the entire term of contract and extension(s), if any.

TCO = Recurring Charges + One Time Charges + Optional Charges

| Date | Signature of Authorised Signatory | Name of the Authorised Signatory |
| --- | --- | --- |
| Place |  | Designation ……. |
| Seal……. |  |  |

  - Annexure –V: Power of Attorney

(To be executed on non-judicial stamp paper of Rs.500/-)

BY THIS POWER OF ATTORNEY executed on _____________________, 2018, We _______________, a Company within the meaning of the Companies Act, 2013, having its Registered Office at ______________________ (hereinafter referred to as “the Company”) doth hereby nominate, constitute and appoint <Name>, <Employee no.>, < Designation> of the Company, as its duly constituted Attorney, in the name and on behalf of the Company to do and execute any or all of the following acts, deeds, matters and things, namely :-

Execute and submit on behalf of the Company a Proposal and other papers / documents with ‘Small Industries Development Bank of India’ (“SIDBI”) relating to ‘Request for proposal No. 400/2019/1338/BYO/ITV dated May 29, 2018 for Co-location of Bank’s Disaster Recovery Site and to attend meetings and hold discussions on behalf of the Company with SIDBI in this regard.

THE COMPANY DOTH hereby agree and undertake to ratify and confirm all whatsoever the attorney shall lawfully do or cause to be done under or by virtue of these presents including anything done after revocation hereof but prior to actual or express notice thereof being received by the person or persons for the time being dealing with the attorney hereunder.

IN WITNESS WHEREOF, _______________________ has caused these presents to be executed by _______________________ on the day, month and year mentioned hereinabove.

For and on behalf of the Board of Directors of

_____________________

I  Accept

……………………..   (Signature)

(Name Title and Address of the Attorney)

  - Annexure –VI: Non-Blacklisting

Place: ___________________

Date: ____________________

To

The Dy. General Manager [Systems]

Small Industries Development Bank of India

MSME Development Center, 3rd Floor

Information Technology Vertical

Plot No.C-11, G Block

Bandra Kurla Complex

Bandra [East]

Mumbai 400 051

Dear Sir,

Non-Blacklisting

We _________________________________ (bidder name), hereby declare, confirm and undertake that:

- We are not blacklisted by Public Financial Institutions, Public Sector Bank, RBI or IBA or any other Government  or Government agencies, regulators as on the date of RfP.

- We also undertake that, we are not involved in any legal case that may affect the solvency / existence of our firm or in any other way that may affect capability to provide / continue the services to bank.

Yours faithfully,

Authorized Signatories

Name: ______________________________

Designation: _________________________

Company Seal:

  - Annexure –VII: EMD / Bid Security Form

(Sample Format - TO BE EXECUTED ON A NON-JUDICIAL STAMPED PAPER)

To: SMALL INDUSTRIES DEVELOPMENT BANK OF INDIA

WHEREAS …………………………………………………….. (Name of Vendor) (hereinafter called the ‘the Vendor”) has undertaken, in pursuance of Request for Proposal (RFP) No. 400/2019/1338/BYO/ITV dated May 29, 2018 to _________________________ (Herein after called the ‘the RFP”) to you.

AND WHEREAS, it has been stipulated by you in the said RFP that the Vendor shall furnish you with a Bank Guarantee from a commercial Bank for the sum specified therein, as security for compliance with the Vendor’s performance obligations in accordance with the RFP.

AND WHEREAS we ----------------Bank having its registered office at ----- and inter alia a branch office situated at ------- have agreed to give a performance guarantee in lieu of EMD of ` --------- (Rupees ------------------ only) on behalf of the Vendor.

We -------------------Bank further undertake not to revoke and make ineffective the guarantee during it’s currency except with the previous consent of the buyer in writing.

We ------ Bank do hereby unconditionally and irrevocably undertake to pay to SIDBI without any demur or protest, merely on demand from SIDBI, an amount not exceeding Rs.  ---------- (--------- only) by reason of any breach of the terms of the RFP dated ---- by vendor. We hereby agree that the decision of the SIDBI regarding breach of the terms of the RFP shall be final, conclusive and binding

WE do hereby guarantee and undertake to pay forthwith without demur, on demand to SIDBI a sum not exceeding `……………/-. (Rupees ………………………….. …only) (amount of the Guarantee in words and figures) and we undertake to pay you upon your first written demand declaring the Vendor to be in default under the RFP and without cavil or argument, any sum or sums within the limit of `……………/-. (Rupees …………………………..… only) (Amount of guarantee) as aforesaid, without your needing to prove or to show grounds or reasons for your demand or the sum specified therein.

Our obligation to make payment under this Guarantee shall be a primary, independent and absolute obligation and we shall not be entitled to delay or withhold payment for any reason. Our obligations hereunder shall not be affected by any act, omission, matter or thing which but for this provision might operate to release or otherwise exonerate us from our obligations hereunder in whole or in part, including and whether or not known to us or you:

- Any time or waiver granted to the vendor;

- The taking, variation, compromise, renewal or release of or refusal or neglect to perfect or enforce any rights, remedies or securities against the vendor;

- Any Variation of or amendment to the RFP or any other document or security so that references to the Contract in this Guarantee shall include each such Variation and amendment;

- any unenforceability, invalidity or frustration of any obligation of the VENDOR or any other person under the RFP or any other document or security waiver by you of any of the terms provisions conditions obligations UNDER RFP or any failure to make demand upon or take action against the VENDOR;

- any other fact, circumstance, provision of statute or rule of law which might, were our liability to be secondary rather than primary, entitle us to be released in whole or in part from our undertaking; and;

- any change in constitution of the vendor;

- any petition for the winding up of the VENDOR has been admitted and a liquidator or provisional liquidator has been appointed or an order of bankruptcy or an order for the winding up or dissolution of the vendor has been made by a Court of competent jurisdiction;

The written demand referred to in paragraph above shall be deemed to be sufficiently served on us if you deliver to us at the address as set out in paragraph 3.

This guarantee is valid until the ………..  day of …………. And a claim in writing is required to be presented to us within three months from       i.e. on or before ----all your rights will be forfeited and we shall be relieved of and discharged from all our liabilities mentioned hereinabove.

Signature and Seal of Guarantors (Vendor’s Bank)

…………………………………………………………..

Date…………………………………………………….

Address …………………………………………………

……………………………………………………………

……………………………………………………………

  - Annexure –VIII: Pre-Contract Integrity Pact

(To be executed on Non-Judicial Stamp Paper of Rs.100/-)

- General

This pre-bid-pre-contract Agreement (hereinafter called the Integrity Pact) is made at _________ place___ on ---- day of the month of -----, 2018 between Small Industries Development Bank of India, having its Head Office at 15, Ashok Marg, Lucknow – 226001 and inter alia, its Mumbai Office at MSME Development Centre, C-11, G-Block, Bandra-Kurla Complex, Bandra(E), Mumbai 400051 (hereinafter called the “BUYER”/SIDBI, which expression shall mean and include, unless the context otherwise requires, its successors and assigns) of the First Part and M/s --- represented by Shri ----, Chief Executive Officer (hereinafter called the “BIDDER/Seller” which expression shall mean and include, unless the context otherwise requires, his successors and permitted assigns) of the Second Part.

WHEREAS the BUYER proposes to co-locate its DR site and the BIDDER/Seller is willing to offer/has offered the services and

WHEREAS the BIDDER is a private company/ public company/ Government undertaking/partnership/ registered export agency, constituted in accordance with the relevant law in the matter and the BUYER is a corporation set up under an Act of Parliament.

NOW, THEREFORE,

To avoid all forms of corruption by following a system that is fair, transparent and free from any influence /prejudiced dealing prior to, during and subsequent to the currency of the contract to be entered into with a view to:-

- Enabling the BUYER to obtain the desired said stores/equipment/services at a competitive price in conformity with the defined specifications by avoiding the high cost and the distortionary impact of corruption on public procurement and

- Enabling BIDDERs to abstain from bribing or indulging in any corrupt practice in order to secure the contract by providing assurance to them that their competitors will also abstain from bribing and other corrupt practices and the BUYER will commit to prevent corruption in any form by its officials by following transparent procedures.

The parties hereto hereby agree to enter into this integrity Pact and agree as follows:

- Commitments of the BUYER

  - The BUYER undertakes that no official of the BUYER, connected directly or indirectly with the contract, will demand, take a promise for or accept, directly or through intermediaries, any bribe, consideration, gift, reward, favour or any material or immaterial benefit or any other advantage from the BIDDER, either for themselves or for any person, organization or third party related to the contract in exchange for an advantage in the bidding process, bid evaluation, contracting or implementation process related to the contract.

  - The BUYER will during the pre-contract stage, treat all BIDDERs alike, and will provide to all BIDDERs the same information and will not provide any such information to any particular BIDDER which could afford an advantage to that particular BIDDER in comparison to other BIDDERs.

  - All the officials of the BUYER will report to the appropriate Government office any attempted or completed breaches of the above commitments as well as any substantial suspicion of such a breach.

  - In case any such preceding misconduct on the part of such official(s) is reported by the BIDDER to the BUYER with full and verifiable facts and the same is prima facia found to be correct by the BUYER, necessary disciplinary proceedings, or any other action as deemed fit, including criminal proceedings may be initiated by the BUYER and during such a period shall be debarred from further dealings related to the contract process.  In such a case while an enquiry is being conducted by the BUYER the proceedings under the contract would not be stalled.

- Commitments of BIDDERs

The BIDDER commits itself to take all measures necessary to prevent corrupt practices, unfair means and illegal activities during any stage of its bid or during any pre-contract or post-contact stage in order to secure the contract or in furtherance to secure it and in particular commit itself to the following: -

  - The BIDDER will not offer, directly or through intermediaries, any bribe, gift, consideration, reward, favour, any material or immaterial benefit or other advantage, commission, fees, brokerage or inducement to any officials of the BUYER, connected directly or indirectly with bidding process, or to any person, organization or third party related to the contract in exchange for any advantage in the bidding, evaluation, contracting and implementation of the contract.

  - The BIDDER further undertakes that it has not given, offered or promised to give, directly or indirectly any bribe , gift, consideration, reward, favour, any material or immaterial benefit or other advantage, commission, fees, brokerage or inducement to any official of the BUYER or otherwise in procuring the Contract or forbearing to do or having done any act in relation to the obtaining or execution of the contract or any other contract with the Government for showing or forbearing to show favour or disfavor to any person in relation to the contract or any other contract with the Government.

  - BIDDERs shall disclose the name and address of agents and representatives and Indian BIDDERs shall disclose their foreign principals or associates.

  - BIDDERs shall disclose the payments to be made by them to agents/brokers or any other intermediary, in connection with this bid/contract.

  - The BIDDER further confirms and declares to the BUYER that the BIDDER is the original manufacture/integrator/authorized government sponsored export entity of the defence stores and has not engaged any individual or firm or company whether Indian or foreign to intercede, facilitate or any way to recommend to the BUYER or any of its functionaries, whether officially or unofficially to the award of the contract to the BIDDER	, or has any amount been paid, promised or intended to be paid to any such individual, firm or company in respect of any such intercession, facilitation or recommendation.

  - The BIDDER, either while presenting the bid or during pre-contract negotiations or before signing the contract, shall disclose any payments he has made, is committed to or intends to make to officials of the BUYER or their family members, agents, brokers or any other intermediaries in connection with contract and the details of services agree upon for such payments.

  - The BIDDER will not collude with other parties interested in the contract to impair the transparency, fairness and progress of the bidding process, bid evaluation, contracting and implementation of the contract.

  - The BIDDER will not accept any advantage in exchange for any corrupt practice, unfair means and illegal activities.

  - The BIDDER shall not use improperly, for purposes of competition or personal gain or pass on the others, any information provided by the BUYER as part of the business relationship, regarding plans, technical proposals and business details, including information contained in any electronic data carrier.  The BIDDER also undertakes to exercise due and adequate care lest any such information is divulged.

  - The BIDDER commits to refrain from giving any complaint directly or through any other manner without supporting it with full and verifiable facts.

  - The BIDDER shall not instigate or cause to instigate any third person to commit any of the actions mentioned above.

  - if the BIDDER or any employee of the BIDDER or any person acting on behalf of the BIDDER, either directly or indirectly, is a relative to any of the officers of the BUYER or alternatively, if any relative of the officer of the BUYER has financial interest/stake in the BIDDER’s firm, the same shall be disclosed by the BIDDER at the time of filling of tender.

The term ‘relative’ for this purpose would be as defined in Section 2 (77) of the Companies Act, 2013.

  - The BIDDER shall not lend to or borrow any money from or enter into any monetary dealings or transactions, directly or indirectly, with any employee of the BUYER.

- Previous Transgression

  - The BIDDER declares that no previous transgression occurred in the last three years immediately before signing of this integrity Pact, with any other company in any country in respect of any corrupt practices envisaged hereunder or with any Public Sector Enterprise in India or any Government Department in India that could justify BIDDER’s exclusion from the tender process.

  - The BIDDER agrees that if it makes incorrect statement on this subject, BIDDER can be disqualified from the tender process or the contract, if already awarded, can be terminated for such reason.

- Earnest Money (Security Deposit)

  - While submitting commercial bid, the BIDDER shall deposit an amount Rs.            /-  as Earnest Money/Security Deposit, with the BUYER through any of the following instrument.

- Bank Draft or a Pay Order in favour of Small Industries Bank of India, Payable at Mumbai.

- A confirmed guarantee by an Indian Nationalized Bank, promising payment of the guaranteed sum to the BUYER immediately on demand without any demur whatsoever and without seeking any reasons whatsoever. The demand for payment by the BUYER shall be treated as conclusive proof of payment.

  - Earnest Money/Security Deposit shall be valid till the date of bid validity as mentioned in the RfP.

  - In case of the successful BIDDER a clause would also be incorporated in the Article pertaining to Performance Bond in the Purchase Contract that the provision of Sanctions for Violation shall be applicable for forfeiture of Performance Bond in case of a decision by the BUYER to forfeit the same without assigning any reason for imposing sanction for violation of this Pact.

  - No interest shall be payable by the BUYER to the BIDDER on Earnest Money/Security Deposit for the period of its currency.

- Sanctions for Violations

  - Any breach of the aforesaid provision by the BIDDER or any one employed by it or acting on its behalf (whether with or without the knowledge of the BIDDER) shall entitle the BUYER to take all or any one of the following actions, wherever required:-

- To immediately call off the pre-contract negations without assigning any reason or giving any compensation to the BIDDER.  However, the proceedings with other BIDDER(s) would continue

- The Earnest Money Deposit (in pre-contract stage) and /or Security Deposit/Performance Bond) (after the contract is signed) shall stand forfeited either fully or partially, as decided by the BUYER and the BUYER shall not be required to assign any reason therefore.

- To immediately cancel the contract, if already signed, without giving any compensation to the BIDDER

- To recover all sums already paid by the BUYER, and in case of Indian BIDDER with interest thereon at 2% higher than the prevailing Prime Lending Rate of State Bank of India, while in case of a bidder from a country other than India with interest thereon at 2% higher than LIBOR.  If any outstanding payment is due to the bidder from the buyer in connection with any other contract for any other stores, such outstanding payment could also be utilized to recover the aforesaid sum and interest.

- To encash the advance bank guarantee and performance bond/warranty bond, if furnished by the BIDDER, in order to recover the payments, already made by the BUYER along with interest.

- To cancel all or any other Contracts with the BIDDER, the BIDDER shall be liable to pay compensation for any loss or damage to the BUYER resulting from such cancellation/rescission and the BUYER shall be entitled to deduct the amount so payable from the money(s) due to the BIDDER

- To debar the BIDDER from participating in future bidding processes of the buyer or its associates or subsidiaries for minimum period of five years, which may be further extended at the discretion of the BUYER.

- To recover all sums paid in violation of this Pact by BIDDER(s) to any middleman or agent or broker with a view to securing the contract.

- In cases where irrevocable Letters of Credit have been received in respect of any contract signed by the BUYER with BIDER, the same shall not be opened.

- Forfeiture of Performance Bond in case of decision by the BUYER to forfeit the same without assigning any reason for imposing sanction for violation of this Pact.

  - The BUYER will be entitled to take all or any of the actions mentioned at para 6.1(i) to (x) of this Pact also on the commission by the BIDDER or any one employed by it or acting on its behalf (whether with or without the knowledge of the BIDDER), of an offence as defied in Chapter IX of the Indian Penal code, 1860 or Prevention of Corruption Act, 1988 or any other statute enacted for prevention of corruption.

  - The decision of the BUYER to the effect that a breach of the provision of this Pact has been committed by the BIDDER shall be final and conclusive on the BIDDER.  However, the BIDDER can approach the independent Monitor(s) appointed for the purposes of this Pact.

- Fall Clause

  - The BIDDER undertakes that it has not supplied/is not supplying similar products /systems or subsystems at a price lower than that offered in the present bid in respect of any other Ministry/Department of the Government of India or PSU and if it is found at any stage that similar product/systems or sub systems was supplied by the BIDDER to any other Ministry/Department of the Government of India or a PSU at a lower price, then that very price, with due allowance for elapsed time, will be applicable to the present case and the difference in the cost would be refunded by the BIDDER to the BUYER, if the contract has already been concluded.

- Independent Monitors

  - The bank has appointed Independent Monitors (hereinafter referred to as Monitors) for this Pact in consultation with the Central Vigilance Commission. Details of Independent Monitor are:

Shri. Ashok Sinha, (IAS retd.),

13 Yayati, Sector-58A, Nerul (West),

Palm Beach Road, Navi-Mumbai 400706

Ph: 9821844044, Mail id: asinha51@gmail.com

  - The task of the Monitors shall be to review independently and objectively, whether and to what extent the parties comply with the obligations under this Pact.

  - The Monitors shall not be subject to instruction by the representatives of the parties and perform their functions neutrally and independently.

  - Both the parties accept that the Monitors have the right to access all the documents relating to the project/procurement, including minutes of meetings.

  - As soon as the Monitor notices or has reason to believe, a violation of the Pact, he will so inform the Authority designated by the BUYER

  - The BIDDER(s) accepts that the Monitor has the right to access without restriction to all Project documentation of the BUYER including that provided by the BIDDER.  The BIDDER will also grant the Monitor, upon his request and demonstration of a valid interest, unrestricted and unconditional access to his project documents.  The same is applicable to Subcontractors.  The Monitor shall be under contractual obligation to treat the information and documents of the BIDDER/Subcontractor(s) with confidentiality

  - The BUYER will provide to the Monitor sufficient information about all meetings among the parties related to the Project provided such meetings could have an impact on the contractual relations between the parties.  The parties will offer to the Monitor the option to participate in such meetings

  - The Monitor will submit a written report to the designed Authority of the BUYER within 8 to 10 weeks from the date of reference or intimation to him by the BUYER/BIDDER and should the occasion arise, submit proposals for correcting problematic situations.

- Facilitation of Investigation

In case of any allegation of violation of any provision of this Pact or payment of commission, the BUYER or its agencies shall be entitled to examine all the documents including the Books of Accounts of the BIDDER and the BIDDER shall provide necessary information and documents in English and shall extend all possible help for the purpose of such examination.

- Law and Place of Jurisdiction

This Pact is subject to Indian Law.  The place of performance and jurisdiction is the seat of the BUYER.

- Other Legal Actions

The action stipulated in this integrity Pact are without prejudice to any other legal action that may follow in accordance with the provisions of the extant law in force relating to any civil or criminal proceedings.

- Validity

  - The validity of this Integrity Pact shall be from date of its signing and extend upto 5 years or the complete execution of the contract to the satisfaction of both the BUYER and the BIDDER/Seller, including warranty period, whichever is later. In case BIDDER is unsuccessful, this integrity Pact shall expire after six months from the date of the signing of the contract.

  - Should one or several provisions of the Pact turn out to be invalid, the remainder of this Pact shall remain valid.  In this case, the parties will strive to come to an agreement to their original intentions.

  - A person signing the Pact shall not approach the Court while representing the matter to IEM and he/she will await his decision in the matter.

- The parties hereby sign this integrity Pact, at _______________ on ________________

BUYER							BIDDER

Name of the Officer

Designation 							CHIEF EXECUTIVE OFFICER

SIDBI

Witness							Witness

1.______________					1.___________________

2._____________					2.___________________

  - Annexure -IX: Undertaking from Bidder Regarding Ownership of Site

To

The Dy. General Manager [Systems]

Small Industries Development Bank of India

MSME Development Center, 3rd Floor

Information Technology Vertical

Plot No.C-11, G Block

Bandra Kurla Complex

Bandra [East]

Mumbai 400 051

Undertaking of ownership of site / premises proposed for Data Centre for the bank (in case of owned site) OR Undertaking of unexpired lease period on the proposed Data Centre period for the bank (in case of leased premises)

Dear Sir,

- In case of owned sites

We hereby declare, confirm and undertake that the following site address proposed by us to the Bank as Data Center, is owned premise and has been registered in the name of M/S (Service provider name) vide sale deed # (XX) dated XX XX XXXX with the office of the Sub-Registrar at ________________:

| Site Details | Chennai (for Banks DR Site) |
| --- | --- |
| Address of the site proposed to the Bank |  |
| Sale Agreement Reference # |  |
| Sale Agreement Date |  |

- In case of leased site

We hereby declare, confirm and undertake that the following site address proposed by us to the bank as Data Centre, has been a leased premise vide lease deed dated XX XX XXXX, between M/S (Service provider name) and (Name of the Lessor) which is registered with the office of sub-registrar at _________________. The details of the lease period for the premises are as mentioned below:

| Site Details | Chennai (for Banks DR Site) |
| --- | --- |
| Address of the site proposed to the Bank |  |
| Lease deed Date |  |
| Validity of the lease Period |  |
| Name of the lessor |  |
| Unexpired lease period as on RfP due date. |  |

Please note that the sale / lease deed copies (whichever applicable) are enclosed herewith as supporting documents and the same has been duly stamped and registered in accordance with the applicable laws.

Kindly refer to us in case of any clarifications.

Authorized Signatories

Name: ______________________________

Designation: _________________________

Company Seal:

Date :________________________________

  - Annexure –X: Statement of Deviations

Bidder is required to provide details of all deviations, comments and observations or suggestions in the following format with seal and signature.  It also needs to provide a reference of the page number, state the clarification point as stated in tender document and the comment/ suggestion/ deviation that you propose as shown below.

SIDBI may at its sole discretion accept or reject all or any of the deviations, however it may be noted that the acceptance or rejection of any deviation by SIDBI will not entitle the bidder to submit a revised commercial bid. Clarifications on queries given after Pre-bid meeting will not be further entertained.

| Tender No.: 400/2019/1338/BYO/ITV dated May 29, 2018 |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.N. | Page Number | Section Number | Clarification point as stated in the tender document | Comment/ Suggestion/ Deviation |
| 1. |  |  |  |  |
| 2. |  |  |  |  |
| 3. |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |

Authorized Signatories

Name: ______________________________

Designation: _________________________

Company Seal:

  - Annexure –XI: Bank Mandate Form

(दो प्रतियों में प्रस्तुत किया जाए /To be submitted in Duplicate)

| 1 | उधारकर्ता /विक्रेता / आपूर्तिकर्ता का नाम Name of Borrower / vendor / supplier: |  |  |  |
| --- | --- | --- | --- | --- |
| 2 | उधारकर्ता / विक्रेता / आपूर्तिकर्ता का पता / Address of the Borrower / vendor / supplier: |  |  |  |
|  | नगर/City |  | ई-मेल आईडी /E-mail id |  |
|  | पिनकोड Pin Code |  | मोबाइल सं./Mobile:No. |  |
|  | सटीडी कूट के साथ दूरभाष सं./Phone No. with STD code |  |  |  |
| 3 | स्थायी खाता संख्या / Permanent Account Number |  |  |  |
| 4 | एमएसई पंजीकरण/सीए प्रमाणपत्र/ MSE Registration / CA Certificate (यदि लागू हो/if applicable) |  |  |  |

5.  बैंक खाते का विवरण / Particulars of Bank account:

| हिताधिकारी का नाम Beneficiary Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| बैंक का नाम / Bank Name |  |  |  | शाखा का नाम Branch Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| शाखा का स्थान / Branch Place |  |  |  | शाखा का नगर Branch City |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| पिनकोड /PIN Code |  |  |  | शाखा कूट Branch Code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| एमआईसीआर सं./MICR No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| खाते का स्वरूप / Account type |  | बचत/ Saving |  | चालू/Current |  |  |  |  |  |  |  | नक़द उधार Cash Credit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| खाता सं./ Account No. (जैसी चेकबुक में अंकित है/ as appearing in the Cheque book) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Please attach a cancelled cheque of your bank for ensuring accuracy of the bank name, branch name & code and Account Number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IFSC CODE | For RTGS transfer |  |  |  |  |  |  | For NEFT transfer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

6. I hereby declare that the particulars given above are correct and complete.  If any transaction is delayed or not effected for reasons of incomplete or incorrect information, I shall not hold SIDBI / IDBI Bank responsible.  I also undertake to advise any change in the particulars of my account to facilitate updation of records for purpose of credit of amount through RBI RTGS/NEFT.

स्थान/Place   :	_____________

दिनांक/Date     :	_____________		         पार्टी/प्राधिकृत हस्ताक्षरकर्ता के हस्ताक्षर                                                                                                          Signature of the party / Authorized Signatory

…………………………………………………………………………………………………………………

प्रमाणित किया जाता है कि ऊपर दिए गए विवरण हमारे अभिलेख के अनुसार सही हैं।

Certified that particulars furnished above are correct as per our records.

बैंक की मुहर/Bank’s stamp

(बैंक के प्राधिकृत अधिकारी के हस्ताक्ष / Signature of the Authorized Official from the Bank’s)

दिनांक/Date :

  - Annexure -XII: Compliance Statement

(To be submitted on bidder’s letter head)

Declaration

Tender No.: 400/2019/1338/BYO/ITV dated May 29, 2018

| Compliance | Description | Bidder Response (Yes/ No) |
| --- | --- | --- |
| Special Terms & Conditions, General Terms & Conditions | We hereby undertake and agree to abide by all the terms and conditions including annexure, corrigendum(s) etc. stipulated by the Bank in this RfP. (Any deviation may result in disqualification of bids) |  |
| Scope of Work | We certify that the proposal submitted by us is as per the scope of work stipulated in the RfP. (Any deviation may result in disqualification of bids) |  |

Bank reserves the right to reject the bid, if the bid is not submitted in proper format as per RfP.

Authorized Signatories

Name: ______________________________

Designation: _________________________

Company Seal:

Date:

  - Annexure –XIII: Non-Disclosure Agreement

(To be executed on a non-judicial stamped paper of requisite value based on place of execution)

WHEREAS, we, ___________________________________, having Registered Office at __________________________________, hereinafter referred to as the COMPANY, are agreeable to execute “________________________________” as per scope defined in the Request for Proposal (RfP) No. 400/2019/1338/BYO/ITV dated May 29, 2018 for Small Industries Development Bank of India, having its Head office at SIDBI Tower, 15 Ashok Marg, Lucknow, 226001, and Mumbai office at, MSME Development Centre, Plot No. C-11, G Block, Bandra Kurla Complex (BKC), Bandra (E), Mumbai - 400 051 (hereinafter referred to as the BANK) and,

WHEREAS, the COMPANY understands that the information regarding the Bank’s Infrastructure shared by the BANK during execution of project is confidential and/or proprietary to the BANK, and

WHEREAS, the COMPANY understands that in the course of submission of the offer for the said RfP and/or in the aftermath thereof, it may be necessary that the COMPANY may perform certain jobs/duties on the Bank’s properties and/or have access to certain plans, documents, approvals, data or information of the BANK;

NOW THEREFORE, in consideration of the foregoing, the COMPANY agrees to all of the following conditions, in order to induce the BANK to grant the COMPANY specific access to the BANK’s property/information, etc.;

The COMPANY will not publish or disclose to others, nor, use in any services that the COMPANY performs for others, any confidential or proprietary information belonging to the BANK, unless the COMPANY has first obtained the BANK’s written authorisation to do so;

The COMPANY agrees that information and other data shared by the BANK or, prepared or produced by the COMPANY for the purpose of submitting the offer to the BANK in response to the said RfP, will not be disclosed to during or subsequent to submission of the offer to the BANK, to anyone outside the BANK;

The COMPANY shall not, without the BANK’s written consent, disclose the contents of this Request for Proposal (Bid) or any provision thereof, or any specification, plan, pattern, sample or information (to be) furnished by or on behalf of the BANK in connection therewith, to any person(s) other than those employed/engaged by the COMPANY for the purpose of submitting the offer to the BANK and/or for the performance of the Contract in the aftermath. Disclosure to any employed/ engaged person(s) shall be made in confidence and shall extend only so far as necessary for the purposes of such performance.

Yours sincerely,

| Date | Signature of Authorised Signatory … |
| --- | --- |
| Place | Name of the Authorised Signatory … |
|  | Designation … |
|  | Seal … |

  - Annexure –XIV: Performance Guarantee Format

(TO BE EXECUTED ON A NON-JUDICIAL STAMPED PAPER OF APPROPRIATE VALUE)

KNOW ALL MEN BY THESE PRESENTS that in consideration of the Small Industries Development Bank of India (SIDBI), a Corporation established under the Small Industries Development Bank of India Act, 1989, and having its Head Office at SIDBI Tower, 15 Ashok Marg, Lucknow, 226001, and Mumbai office at 3rd Floor, MSME Development Centre, Plot No. C-11, G Block, Bandra Kurla Complex (BKC), Bandra (E), Mumbai - 400 051 (hereinafter called the Corporation / Bank) having agreed to accept from M/s. ‘Vendor Name’ having its office at ‘Vendor’s Office Address’, (hereinafter called "the Vendor") an agreement of guarantee for Rs. _______ (Rupees _____________________ only), for the due fulfillment by the vendor of the terms and conditions of the Purchase order No. ________________ dated __________ made between the vendor and the Corporation for providing services for SIDBI’s ‘Project Details’   hereinafter called "the said Agreement”).

- We, Bank (Bank Name and Details), do hereby undertake to indemnify and keep indemnified the Corporation to the extent of Rs. _______ (Rupees _____________________ only) against any loss or damage caused to or suffered by the Corporation during warranty period by reason of any breach by the Vendor of any of the terms and conditions contained in the said Agreement of which breach the opinion of the Corporation shall be final and conclusive.

- We Bank (Bank Name and Details),  do hereby guarantee and undertake to pay forthwith on demand without demur to the Corporation such sum not exceeding the said sum of Rs. _______ (Rupees _____________________ only) as may be specified in such demand, in the event of the vendor failing or neglecting to execute fully efficiently and satisfactorily the order for implementation services for the ‘Project Details’   placed with it (the work tendered for by it) within the period stipulated in the said Agreement in accordance with the design, specification, terms and conditions contained or referred to in the said Agreement or in the event of the Vendor refusing or neglecting to maintain satisfactory operation of the equipment or work or to make good any defect therein notified by the Corporation to the vendor during the warranty period or otherwise to comply with and conform to the design, specification, terms and conditions contained or referred to in the said Agreement.

- We, Bank (Bank Name and Details), further agree that the guarantee herein contained shall remain in full force and effect during the period that would be taken for the performance of the said order as laid down in the said agreement including the "Warranty obligations" or till validity date of this guarantee i.e. upto  ________, whichever is earlier and subject to the terms of the "the said Agreement” it shall continue to be enforceable for the breach of warranty conditions within warranty period  and till all the defects notified by the Corporation to the vendor during the warranty period have been made good to the satisfaction of Corporation & the Corporation or its authorized representative certified that the terms and conditions of the said agreement have been fully and properly complied with by the vendor or till validity of this guarantee i.e _________, whichever is earlier, and

- We, Bank (Bank Name and Details), may extend the validity of Bank Guarantee at the request of the Vendor for further period or periods from time to time beyond its present validity period, but at our sole discretion.

- The liability under this guarantee is restricted to Rupees ________/-  only and will expire on _________  and unless a claim in writing is presented to us at Bank (Bank Name and Details)  within 6 months from _________ , i.e. on or before _________, all your rights will be forfeited and we shall be relieved of and discharged from all our liabilities there-under.

- The Guarantee herein contained shall not be determined or affected by Liquidation or winding up or insolvency or closure or any other corporate / structural change of the Vendor.

- The executant has the power to issue this guarantee and executants on behalf of the Bank and hold full and valid Power of Attorney granted in their favour by the Bank authorising them to execute this guarantee.

Notwithstanding anything contained here in above, our liability under this guarantee is restricted to Rs. _______ (Rupees _____________________ only). Our guarantee shall remain in force until ________. Our liability hereunder is conditional upon your lodging a demand or claim with Bank (Bank Name and Details) on or before _________. Unless a demand or claim is lodged with Bank (Bank Name and Details) within the aforesaid time, your rights under the guarantee shall be forfeited and we shall not be liable there under. This guarantee shall be governed by and construed in accordance with the laws of India. All claims under this guarantee will be made payable at Bank (Bank Name and Details). This Guarantee will be returned to the Bank when the purpose of the guarantee has been fulfilled or at its expiry, which ever is earlier.

We, Bank (Bank Name and Details) lastly undertake not to revoke this guarantee during its currency except with the previous consent of the Corporation in writing.

In witness where of we ...................... have set and subscribed our hand and seal this ........................day of .........................2018.

SIGNED, SEALED AND DELIVERED.

BY

AT

IN THE PRESENCE OF	WITNESS	:

- Name ..........................

Signature.....................

Designation..................

- Name .............................

Signature.........................

Designation.....................

  - Annexure –XV: Contract Form

[To be executed on Non-Judicial Stamp Paper of appropriate value]

Small Industries Development Bank of India (SIDBI), a Corporation established under the Small Industries Development Bank of India Act, 1989, and having its Head Office at SIDBI Tower, 15 Ashok Marg, Lucknow, 226001, and Mumbai office at 3rd Floor, MSME Development Centre, Plot No. C-11, G Block, Bandra Kurla Complex (BKC), Bandra (E), Mumbai - 400 051 (hereinafter called the Corporation / Bank / Purchaser, which expression shall, unless repugnant to the context or meaning thereof, be deemed to mean and include its successor and assignee) of one part and M/s ____________________ (Name of the Service provider), a Company/a Firm/ duly registered/incorporated ______________________ Act, having its Registered Office/ Head Office/ Corporate Office at ____________________________ (City & Country of Supplier) (hereinafter referred to as the “the Supplier”, which expression shall, unless repugnant to the context or meaning thereof, be deemed to mean and include its successors and permitted assignee) of Other

Part.

WHEREAS the purchaser is desirous that services related to Data Center co-location and ancillary services should be provided by the service provider viz, ________________ _______________ (Brief Description of Goods and Services) and has accepted a bid by the service provider for services related to Data Center co-location and ancillary services in the sum of Rs._____________________________ (Contract Price in Words and Figures) (hereinafter “the Contract Price”).

NOW THIS AGREEMENT WITNESSETH AS FOLLOWS:

- In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the Conditions of Contract referred to.

- The following documents shall be deemed to form and be read and construed as part of this Agreement along-with RFP, viz.:

- The Bid form and price schedule submitted by the bidder;

- The Scope of Work;

- The Special Terms and Conditions;

- The Service Level Agreement;

- The General Terms and Conditions;

- The Purchaser’s Notification of Award

- However, In case of any conflict clauses between this agreement and the RFP or its enclosures, the spirit in the clauses of RFP shall prevail.

- In consideration of the payments to be made by the Purchaser to the Supplier as hereinafter mentioned, the Supplier hereby covenants with the Purchaser to provide the Goods and Services and to remedy defects therein in conformity in all respects with the provisions of the contract.

- The Purchaser hereby covenants to pay the Supplier in consideration of the provision of the Goods and Services and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

- Other usual convents and conditions related to the contract would be forming part of the contract that will be executed between the parties.

- Brief particulars of the goods and services which shall be supplied/provided by the Supplier are as under:

IN WITNESS whereof the parties hereto have caused this Agreement to be executed in accordance with their respective laws the day and year first above written.

| Signed, Sealed and Delivered by the __________________________ (Name & Designation) for and on behalf of SIDBI, One Part (the Supplier) | Signed, Sealed and Delivered by the __________________________ (Name & Designation) for and on behalf of SIDBI, One Part (the purchaser) |
| --- | --- |

Witness						Witness

1.______________					1.___________________

2._____________					2.___________________

# APPENDIX

  - Appendix -i:- Requirement of Inter-rack Cabling

- DR Site:

  - Appendix -ii: - List of Hardware Items with Power Socket Details

- DR Site

- Power Socket Details

| S.N. | Hardware Details |  | Qty | Rack Space per Device | Power Socket Details |  | Rated power Per SMPS |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Make | Model No. |  |  | Type | Number of SMPS per Device |  |
| A. | Servers |  |  |  |  |  |  |
| 1 | HPE | HP RX 6600 (Unix) | 1 | 7U | C-19, 16A | 2 | 1600W |
| 2 | HPE | HP PROLIENT DL380G6 | 3 | 2U | C-13, 10A | 2 | 460W |
| 3 | HUAWEI | HUAWEI RH2288 | 2 | 2U | C-13, 10A | 2 | 460W |
| 4 | DELL | DELL R710 | 3 | 2U | C-13, 10A | 2 | 570W |
| 5 | DELL | DELL R530 | 2 | 2U | C-13, 10A | 2 | 750W |
| 6 | HPE | HPE ProLiant DL380 Gen 9 | 6 | 2U | C-13, 10A | 2 | 500W |
| 7 | IBM | IBM X 336 | 2 | 1U | C-13, 10A | 1 | 585W |
| 8 | HPE | HPE Proliant DL360 GEN9 | 1 | 1U | C-13, 10A | 2 | 500W |
| B. | SAN Storage / switches and Tape Drive |  |  |  |  |  |  |
| 1 | HPE | SAN EVA - 4400 Storage | 2 | 4U | C-13, 10A | 4 | 575W |
| 2 |  | Ultrium 1840 LTO 4 Tape Drive | 1 | 2U | C-13, 10A | 1 | 125W |
| 3 |  | Storage Works 8/8 SAN Switch | 2 | 1U | C-13, 10A | 1 | 75W |
| 4 | IBM | Ultrium 3580L11 TAPE DRIVE | 2 | 2U | C-13, 10A | 1 | 125W |
| 5 | HPE | 3 PAR 8200 2N Storage | 1 | 5U | C-13, 10A | 5 | 1344W |
| 6 | DELL | Dell LTO6 200 Tape Drive | 2 | 1U | C-13, 10A | 1 | 125W |
| 7 | TANDBERG | Tandberg Overland NEOs – T24 | 1 | 2U | C-13, 10A | 1 | 168W |
| C. | Security Devices |  |  |  |  |  |  |
| 1 | Fortigate | FG 1200D firewall | 2 | 2U | C-13, 10A | 2 | 360W |
| 2 |  | FA200D | 1 | 1U | C-13, 10A | 1 | 450W |
| 3 | Checkpoint | Checkpoint 5900 NGTP | 2 | 1U | C-13, 10A | 2 | 165W |
| 4 | CITRIX | Citrix NetScaler | 1 | 1U | C-13, 10A | 1 | 822W |
| 5 | Blue Coat | SG 200 | 2 | 1U | C-13, 10A | 1 | 450W |
| 6 | Fortigate | FG 60D | 1 | 1U | C-13, 10A | 1 | 65W |
| D. | Network Switches/ Devices |  |  |  |  |  |  |
| 1 | HPE | 7904 | 2 | 2U | C-13, 10A | 2 | 1800W |
| 2 |  | 5930 | 4 | 2U | C-13, 10A | 2 | 400W |
| 3 |  | 5130HI | 4 | 2U | C-13, 10A | 1 | 107W |
| 4 |  | HP -2530 – 24G | 2 | 1U | C-13, 10A | 1 | 247W |
| 5 | Cisco | 3750X | 1 | 1U | C-13, 10A | 2 | 350W |
| 6 | RADWARE Load Balancer | Alteon 5208 | 2 | 1U | C-13, 10A | 2 | 140W |
| E. | Network Hardware (Routers) |  |  |  |  |  |  |
| 1 | Cisco | 2951 | 2 | 2U | C-13, 10A | 2 | 750W |
| 2 |  | 1921 | 1 | 1U | C-13, 10A | 2 | 250W |
| 3 |  | 4321 | 2 | 2U | C-13, 10A | 2 | 250W |
| 4 |  | 800 | 4 | 1U | C-13, 10A | 1 | 60W |

$$ Approximate maximum power rating.

- Power Strip Requirement

- Each rack to be provided with two power strips

- Each power strip should contain 16 numbers of C-13,10A sockets and 4 numbers of C-19, 16A sockets.

*************

End of document