भारतीय लघु उद्योग विकास बैंक

निविदा सं.  404/2015/1089/PNBO 					     दिनांक  02.03.2015

प्रस्ताव निवेदन (आरएफपी) - पुणे में यूपीएस की आपूर्ति और स्थापना

सिडबी अपने ‘जीवन श्री बिल्डिंग’, भू-तल, स.नं.1109, प्लाट नं 488, विद्यापीठ मार्ग, पुणे सेन्ट्रल के पास, शिवाजी नगर, पुणे 411 016, स्थित पुणे कार्यालय के लिए 1 नग 30 केवीए यूपीएस 120 मिनट के बैकअप समय के साथ , की खरीद करने का इरादा रखता है। इस संबंध में आपसे , अनुबंध में दिये प्रारूपों के अनुसार, प्रस्ताव प्रस्तुत करने का अनुरोध हैं:

Annexure I	:	न्यूनतम पात्रता मानदंड

Annexure II	:	सामान्य नियम और शर्तें

Annexure III	:	यूपीएस के तकनीकी विनिर्देश

Annexure IV	:	वाणिज्यिक बोली प्रारूप

Annexure V	:	तकनीकी बोली प्रारूप

Annexure VI	:	पूर्व योग्यता बोली प्रारूप

Annexure VII	:	निर्माता प्राधिकार फार्म [MAF]

तकनीकी और वाणिज्यिक बोलियां दो अलग NON-Window लिफाफे में क्रमश "पुणे में यूपीएस की खरीद के लिए तकनीकी बोली" और " पुणे में यूपीएस की खरीद के लिए वाणिज्यिक बोली" के साथ प्रस्तुत की जाये । इसके अलावा तकनीकी बोली के साथ , पूर्व योग्यता बोली, ईएमडी डिमांड ड्राफ्ट और निर्माता प्राधिकार फार्म , भी शामिल करे । सभी प्रस्ताव 20.03.2015 की शाम 5:30 बजे या पहले, नीचे दिए गए पते पर प्रस्तुत किये जाने चाहिए:

उप महाप्रबंधक, आरओपीएन

भारतीय लघु उद्योग विकास बैंक

‘जीवन श्री बिल्डिंग’,

भू-तल, स.नं.1109,

प्लाट नं 488,

विद्यापीठ मार्ग,

पुणे सेन्ट्रल के पास,

शिवाजी नगर,

पुणे 411 016,

फोन 020-25675269, 25677947, 2568832

सिडबी बिना कोई कारण बताए, किसी भी समय, किसी भी बोली को स्वीकार या अस्वीकार करने का अधिकार सुरक्षित रखता है|

भवदीय

हस्ताक्षर /-

[रवि त्यागी]

महा प्रबंधक

SMALL INDUSTRIES DEVELOPMENT BANK OF INDIA

Tender No.404/2015/1089/PNBO	         					Date :   02.03.2015

Request for Proposal (RFP) - Supply and Installation of UPS at SIDBI, Pune

SIDBI intends to procure 1 no. 30 KVA UPS with a back up time of  2 hours for its Pune office situated at Jeevanm Shree Building, Ground Floor, S.No.1109, Plot No.488, University Road, Near Pune Central Mall, Shivajinagar, Pune 411 016. In this connection you are requested to submit the proposal as per formats given in the following Annexure:

Annexure I	:	Minimum eligibility criteria

Annexure II	:	General Terms and Conditions

Annexure III	:	Technical Specifications of the UPS

Annexure IV	:	Commercial Bid Format

Annexure V	:	Technical Bid Format

Annexure VI	:	Pre-qualification Bid Format

Annexure VII	:	Manufacturer Authorisation Form [MAF]

The technical and commercial bids to be submitted in two separate NON-Window envelopes, superscribing “Technical Bid for purchase of UPS at Pune” and “Commercial Bid for purchase of UPS at Pune” respectively. Further, the technical bid should contain Pre-qualification bid,EMD Demand Draft and MAF. The proposals completed in all respect must be submitted on or before closing hours (5:30 p.m.) of 20.03.2015 at the address given below:

Deputy General Manager

SIDBI, ROPN

Jeevanm Shree Building,

Ground Floor, S.No.1109,

Plot No.488, University Road,

Near Pune Central Mall,

Shivajinagar,

Pune 411 016

Phone 020-25675269, 25677947, 2568832

SIDBI reserves the right to accept or reject any bid at any time without assigning any reasons thereof.

Yours faithfully

Sd/-

[Ravi Tyagi]

Encl: As above 									    General Manager

# Annexure I

Minimum Eligibility Criteria

# Minimum Eligibility Criteria

- The Bidder :

## should be Original Equipment Manufacturers (OEM) / Authorised Dealer (AUD).

## Bidders quoting as Authorised Distributors/dealers of the manufacturer, will be considered provided:

### The Bidder furnishes Authorisation from the Manufacturer in respect of UPS

### The Bidder as authorised agent, has supplied installed and commissioned UPS and batteries of the kind required by the Bank and has provided after sales service satisfactorily and such UPS must be in satisfactory operation for at least 2 years on the date of Bid opening and must be providing annual maintenance services for the above installations.

## should be a Registered Company.

## should be in existence in UPS sales and services business for the last five (5) years

## should have minimum average turnover or Rs.15 Crore per annum from the sale of UPS during the last three (3) years ending March 2014, in case of Bidder not himself the manufacturer. If it is OEM, then turnover should be at least  50 Crore per annum from the sale of UPS during the last three (3) years ending March 2014.***

## Should be a cash profit making company for at least 2 years out of last 3 years as evidenced from the balance sheets.

## should have direct support center at Pune.

## should have successfully delivered and installed at least 10 UPS during last  2 years (Jun 2012 onwards) out of which at least 2 UPS of similar configuration.

- g. should submit the brochure of the proposed UPS.

***If audited figures for any FY are not available, provisional figures may be provided. Supporting the fact the bidder should furnish auditor’s certificate for last three years ending March’ 2014.

*******************************************************************************************

Annexure II

General Terms and Conditions

1.  Cost Details:

The price should include all levies/ taxes like Service tax, Sales Tax, VAT, Transportation, Customs, Excise, traveling charges, support service during warranty etc along with installation of new UPS and removal of all items under buy-back .  Octroi / Entry Tax, if applicable, will be reimbursed extra as at actuals, on production of receipt which should be in the name of SIDBI.  SIDBI will not be in a position to supply Form-C or Form-D and vendor will have to arrange for Form 31 or 32 or any other road permit, if required, on behalf of SIDBI.

# 2. Earnest Money Deposit [EMD]

## 2.1 Vendor is required to submit a Demand Draft of Rs.20,000/- (Rupees Twenty Thousand Only) towards Earnest Money Deposit drawn in favour of  “Small Industries Development Bank of India [SIDBI]” ,  payable at PUNE  along with the Technical Proposal in order to be eligible for participation.

## 2.2 No interest shall be paid on EMD.

## 2.3 Unsuccessful bidder’s EMD will be discharged/ returned without any interest within 2 weeks from the date of bid validity or upon receipt of signed contract and performance security from the successful bidder, whichever is earlier.

## 2.4 The EMD will be forfeited

### 2.4.1   If a bidder withdraws his bid during the period of bid validity.

### 2.4.2   In case of successful bidder, if the bidder dishonors its bidding commitments.

2.4.3  The successful bidder’s  the EMD shall be refunded at the time for release of final payment., after 	submission of performance Bank guarantee for a sum equivalent to 10% of the order value.

2.5 	 SIDBI is governed by provisions of the Public Procurement Policy for Micro and Small Enterprises (MSEs) as circulated by The Ministry of MSME, GoI. 2.5.1 These provisions shall be applicable to Micro and Small Enterprises (MSEs)  registered with District Industries Centers or Khadi and Village Industries Commission or Khadi and Village Industries Board or Coir Board or National Small Industries Corporation or Directorate of Handicrafts and Handloom or any other body specified by Ministry of Micro, Small and Medium Enterprises

(MSMEs).

2.5.2 Such MSEs would be entitled for exemption from furnishing tender fee and earnest money deposit (EMD). In case of any issue on the subject matter, the MSE’s may approach the tender inviting authority to resolve their grievances. 2.5.3 Agencies/ Bidders desirous of availing exemptions/ preference under above provisions should submit a copy of proof of Registration as MSEs/ and ownership of the same by SC/ST along with the tender/RFP.

Bidder is required to inform its MSME status as per following definition, if applicable.

| Enterprise Category | Manufacturing (Original Investment in P&M) | Services (Original Investment in Equipment) |
| --- | --- | --- |
| Micro | Up to ` 25 lakh | Up to ` 10 lakh |
| Small | Up to ` 500 lakh | Up to ` 200 lakh |
| Medium | Up to ` 1000 lakh | Up to ` 500 lakh |

# 3. Period of validity of bids   Date till which the bids should be valid

90 days from the last date of submission of tender document ie., till  20.06.2015 and shall be binding on the bidder, if Bank chooses to place the purchase order (PO) or repeat order(s), on or before that date. Bank, however, reserves the right to call for fresh quotes at any time during the period, if considered necessary.

4.   Payment Terms:

The standard payment terms of SIDBI are given below.

    - 90% after  delivery and verification of items at Pune.

    - 10% after acceptance of UPS by SIDBI and submission of Performance Bank Guarantee equivalent amount of 10%, valid for a period of 13 months from the date of Acceptance.

Vendor will be required to furnish the documentary proof of delivery and installation and acceptance duly signed by SIDBI while claiming the payment.

Others:

Buy-back details of old items ,  and AMC Charges for a period of 5 years [with same scope as warranty ] after expiry of warranty   will be considered for calculating TCO.

5.   Terms of Delivery :

All items should be delivered within Three weeks(21 days) from the date of purchase order at   SIDBI office. The exact address of the delivery location is as under:

Assistant General Manager(Systems)

SIDBI,

Jeevanm Shree Building,

Ground Floor, S.No.1109,

Plot No.488, University Road,

Near Pune Central Mall,

Shivajinagar,

Pune 411 016

Vendor will have to verify all the items within two days from the date of delivery in the presence of SIDBI officials.

6.   Insurance:

All the ordered hardware items should be insured till one month beyond the date of delivery at the respective location.

7    Penalty for Default Delivery:

If the vendor fails to deliver the items within three weeks(21 days) from the date of the order, SIDBI will impose a penalty of 1% of the order value for the late delivered item for each weeks delay or part thereof, subject to maximum of 10% of value of the late delivered items. In case the delay exceeds five weeks, SIDBI reserves the right to cancel the order. In such an event vendor will not be entitled to or recover from SIDBI any amount by ways of damages, loss or otherwise.

8.     Scope of Work, Installation & Acceptance :

- Delivery of UPS, Batteries and related software/accessories.

- Installations and configuration of the UPS at Pune within 2 weeks of delivery.

- Conduct test and checks and also demonstrate all the features of the UPS (like load, metering, indicators etc.) to SIDBI Officers.

The Hardware/Software will be deemed to be accepted only after it is configured to SIDBI’s requirements as given above.

9.    On-site comprehensive warranty:

The vendor will warrant the UPS, batteries and accompanied software/accessories against defects arising out of faulty design, materials and media workmanship etc. for a period of one year from the date of acceptance. The vendor will provide support for all components and software during the warranty period. Defective hardware shall be replaced by the vendor at his own cost, including the cost of transport. Vendor's hardware engineer will report at SIDBI office within two hours of reporting of breakdown through telephone/email or Fax or courier at the vendor's nearest office and repair the same at the earliest. The downtime of a machine at any location should not exceed 5% in a month. The monthly downtime percent of a machine should be calculated as under :

Downtime % = ( Unavailable hours due to breakdown - PM hours)

----------------------------------------------------------------   X   100

(Available Hours)

Available hours = No. of working days X 8

If the downtime percentage exceeds 5% in a month, the warranty period for the hardware will be extended accordingly.

Preventitive maintenance will be done on quarterly basis by vendor.

10.   Post Warranty Maintenance:

The selected vendor will enter into AMC (Annual Maintenance Contract) with SIDBI, if so desired by SIDBI, for post warranty maintenance, at a rate agreed at the time of purchase. The hardware supplied should be maintained by the vendor for at least 5 years after the expiry of warranty period.

11. Performance Bank Guarantee:

The Vendor will furnish an unconditional Bank Guarantee, executed in Pune, of an amount equivalent to 10% of contract value and valid for a period of 13 months from the date of acceptance of the hardware for indemnifying SIDBI against any default / failure in execution of contract , as per the format provided by SIDBI.  Proforma of the bank guarantee shall be provided to the contracted vendor at the time of placing the order.

12.  Force Majeure:

If the performance as specified in this order is prevented, restricted, delayed or interfered by reason of Fire, explosion, cyclone, floods, War, revolution, acts of public enemies, blockage or embargo, Any law, order, proclamation, ordinance, demand or requirements of any  Government or authority or representative of any such Government including restrict trade practices or regulations, Strikes, shutdowns or labour disputes which are not instigated for the purpose of avoiding obligations herein, or Any other circumstances beyond the control of the party affected, then notwithstanding anything herebefore contained, the party affected shall be excused from its performance to the extent such performance relates to prevention, restriction, delay or interference and provided the party so affected uses its best efforts to remove such cause of non-performance and when removed the party shall continue performance with utmost dispatch.

13.  Arbitration :

In the event of a dispute or difference or difference of any nature whatsoever between the vendor and SIDBI during the course of the assignment arising as a result of this order, the same will be referred for arbitration to a Board of arbitration. This Board will be constituted prior to the commencement of the arbitration and will comprise two arbitrators and an umpire. Vendor and SIDBI will each nominate an arbitrator to the Board and these arbitrators will appoint the umpire. Arbitration will be carried out at a place mutually decided by Vendor and SIDBI.

14.   Indemnity:

The vendor will indemnify SIDBI against any claims due to vendor's violation of any patents and copy rights, in such a form as prescribed by SIDBI.

15.   Contact Information:

Should you require any further clarifications, you may contact Ms MSRK Murthy, Manager, SIDBI, Pune.

*************************************************************************************

Technical Specifications of 30 KVA UPS

| A. General |  |
| --- | --- |
| UPS rating | 30 KVA |
| Topology | True On-line Pulse Width Modulation(PWM) Technology with IGBT’s |
| B. INPUT |  |
| Voltage | 400V AC |
| Input Voltage Range | -20% +20% |
| Input Frequency range | 47-53 Hz |
| Power factor | >= 0.80 |
| Phase | 3 phase, Four wire |
| C. OUTPUT |  |
| Rated Power | 30 KVA |
| Frequency | 50 Hz |
| Voltage | 220/230 V AC |
| Voltage Regulation | +/- 1 % |
| Phase | Single |
| Overload | 120% for 10 min ; 150% for 10 sec |
| Waveform | Sine Wave |
| Response Time | <60 milli sec to reach within +/- 2 % |
| Inverter effeciciency | >=80% |
| D. BATTERY |  |
| Type | Sealed maintenance free with battery rack, switch and connectors |
| Backup | 120 mins at full load |
| Recharge time | 8-10 hours |
| Battery Brand | Exide/ Panasonic/ Global Yuasa(Rocket)/Amron |
| Minimum VAH Required | 28,980 VAH |
| E. Other Requirement |  |
| Indicator to show status of : | Mains on, Inverter on, Battery on charge, Battery over/ under voltage, UPS Overload, Phase fail, Over Heat |
| Protections | Mains Over/Under Voltage, Phase Fail, DC Over/Under Voltage, Inverter Over/Under Voltage, Inverter Overload, Overheat, Built-in Soft/Cold Start and Snubber Circuits for Devices |
| Isolation transformer | Yes |

****************************************************************************************

ANNEXURE IV

FORMAT - Commercial Bid

UPS Brand/Make:  ...........................................................

(Rupees)

| Description | Quantity | Total Price(inclusive of all Taxes) |
| --- | --- | --- |
| UPS - 30 KVA(including 1 year warranty) | 01 |  |
| Batteries (2 Hours backup) |  |  |
| Buy back cost of old UPS(10KVA&5KVA including old batteries) |  |  |
| AMC Rate |  | ...... % |
| AMC Amount for 5 years (After 1 year warrenty) |  |  |
| Grand Total |  |  |

Note:

        - All prices should be inclusive of all levies/ taxes like Service tax, Sales Tax, VAT Transportation, Customs, Excise, traveling charges, support service during warranty etc along with installation of new UPS and removal of all items under buy-back.

        - Prices quoted above should  be valid for a period of 90 days from the date of submission of the proposals.

        - There are two Old UPS (one 10 KVA and one 5 KVA) purchased in Nov 2002 , which are in use at SIDBI Pune office and will have to be taken on buy back .

        - L1 vendor would be arrived based on Grand Total ie.,

[(Cost of new UPSs(incl. 1 year warranty) + new batteries+ AMC for 5 years) minus (cost of old UPS(including old batteries)]

Organization	:

Name		:

Designation	:

Signature	:

Date		:

Place		:

*********************************************************************************************************

ANNEXURE V

FORMAT - Technical Bid

(provide for both UPS separatly)

UPS Brand/Make:  ...........................................................

| A. General |  |
| --- | --- |
| UPS rating |  |
| Topology |  |
| B. INPUT |  |
| Voltage |  |
| Input Voltage Range |  |
| Input Frequency range |  |
| Power factor |  |
| Phase |  |
| C. OUTPUT |  |
| Rated Power |  |
| Frequency |  |
| Voltage |  |
| Voltage Regulation |  |
| Phase |  |
| Overload |  |
| Waveform |  |
| Response Time |  |
| Inverter effeciciency |  |
| D. BATTERY |  |
| Type |  |
| Backup |  |
| Recharge time |  |
| Battery Brand |  |
| Minimum VAH Required |  |
| E. Other Requirement |  |
| Indicator to show status of : |  |
| Protections |  |
| Isolation transformer |  |
| Configuration requirement |  |

** Note: Please attach printed brochures where ever necessary in support of your offering

***To be filled in accordance of Technical specification requirement given in Annexure III

***************************************************************************************************************

Annexure VI

Pre-Qualification Bid

[all fields to be filled in duly and proof of the same to be attached separately, to be submitted with technical bid]

A. Pre-qualification

| Name of the Bidder |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Address of the Bidder |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Telephone: |  |  |  |  |  | Fax: |  |  |  |  | e-mail: |  |  | website: |  |  |  |  |
| 1 | Contact Details of the Person authorised to make commitments to SIDBI |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Designation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Mobile No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | FAX No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | E-mail id |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  | Classification [Tick the appropriate box and attach MAF form as per format given in Annexure III] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | OEM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | AUD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | If, AUD, specify the Name and address of OEM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  | Company Details [Registration certificate to be enclosed] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Type of Company [Govt/PSU/Pub.Ltd/Pvt ltd/ Partnership / Propritory.] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Registration No., and date of registration |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Year of Incorportation / Establishment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Sales Tax Number [copy to be enclosed] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Income Tax Number [copy to be enclosed] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  | Financials [fill in the details and attach proof of the same] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Turnover [in lakh] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 2013-14 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 2012-13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 2011-12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Profit before tax [in lakh] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 2013-14 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 2012-13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 2011-12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  | Service Support |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Whether Local Support Available at Pune [Yes / No] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Address and Telephone No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Working Days and hours |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | No of support engineers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  | References [ to attach proof] Names of two or more buyers (with Names of contact persons, their designations, complete postal address, telephone, tax, telex and e-mail addresses, location of installation etc) to whom similar equipment( 30 KVA rating or more) are supplied installed and commissioned in the past 2 years(July 2012-Jun 2014) and to whom reference may be made by the Bank regarding the Bidder’s technical / delivery / after sales support ability. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Name |  | Address and Contact Details |  |  |  |  | UPS Supplied Details |  |  |  | PO details |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Make | Capacity |  | Qty | PO No and Date [attach PO masking price] |  |  |

Place		:  .......................

Date		:  ........................				Signature with Seal

******************************************************************************

Annexure VII

Manufacturers Authorisation Form [MAF]

[to be submitted along with Technical Bid]

Ref. No:									Date:

To,

Assistant General Manager(Systems)

SIDBI,

Overseas Tower ,

756-L, Anna Salai,

Pune, 600002

Dear Sir,

Sub: RfP No.....................dated .........................for supply of UPS and accessories

We .............................................................. who are established and reputable manufacturers of .......................................................................having factories at .......................................................... and ......................................... do hereby authorise M/s ..................................[Name and address of vendor] to submit a bid and sign the contract with you for the goods manufactured by us aganist the above RfP No............................. dated ..................................

We hereby extend our full guarantee and warranty as per the clauses of contract based on the terms and conditions of the RfP for the goods and services offered for supply by the above firm against the RfP.

Yours faithfully

[                                   ]

Name of the manufacturer

Note: This letter of authority should be on the letterhead of the manufacturer and should be signed by a person competent and having the power of attorney to bind the manufacturer. It should be included by the bidder in its bid.

END OF FILE

*****************************************************************************